## Size
Component | Unit | Total
PV panels | kW | 131.13
Battery bank | kWh | 529.75
Diesel Genset | kW | 32.32

## Cost
Cost item | Component | Scenario | Unit | Total
Weighted Net present cost | System | - | kUSD | 376.18
Net present cost | System | 1 | kUSD | 376.18
Total Investment cost | System | - | kUSD | 147.969
Total fixed O&M cost | System | - | kUSD | 47.479
Total variable O&M cost | System | 1 | kUSD | 184.297
Salvage value | System | - | kUSD | -3.565
Levelized Cost of Energy | System | - | USD/kWh | 0.205
Levelized Cost of Energy scenarios | System | 1 | USD/kWh | 0.205
Investment cost | PV panels | - | kUSD | 107.199
| Battery bank | - | kUSD | 27.841
| Diesel Genset | - | kUSD | 12.928
| National grid | - | kUSD | 0
Fixed cost | PV panels | - | kUSD | 22.3
| Battery bank | - | kUSD | 18.697
| Diesel Genset | - | kUSD | 6.482
| National Grid | - | kUSD | 0
Lost load cost | System | 1 | kUSD | 0
Replacement cost | Battery bank | 1 | kUSD | 27.883
Fuel cost | Diesel | 1 | kUSD | 156.414
Grid electricity cost | National Grid | 1 | kUSD | 0
Grid electricity revenue | National Grid | 1 | kUSD | 0
Fuel CO2 emission | System | 1 | ton | 1060.636
Grid CO2 emission | System | 1 | ton | 0
RES CO2 emission | RES | - | ton | 0
GEN CO2 emission | GEN | - | ton | 0
BESS CO2 emission | BESS | - | ton | 0
TOTAL CO2 emission | System | 1 | ton | 1060.636

## Yearly cash flows
| Fixed costs |  |  |  | Lost load cost | Replacement cost | Fuel cost | Grid cost | Grid revenue
Component | PV panels | Battery bank | Diesel Genset | Grid | System | Battery bank | Diesel | Grid | Grid
Scenario | - | - | - | - | 1 | 1 | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.07 | 0.52 | 0 | 0
Year 2 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.41 | 1.39 | 0 | 0
Year 3 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.49 | 1.78 | 0 | 0
Year 4 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.69 | 4.22 | 0 | 0
Year 5 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.66 | 13.87 | 0 | 0
Year 6 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.64 | 15.21 | 0 | 0
Year 7 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.59 | 28.04 | 0 | 0
Year 8 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.59 | 28.26 | 0 | 0
Year 9 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.58 | 29.76 | 0 | 0
Year 10 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.58 | 30.35 | 0 | 0
Year 11 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.43 | 37.98 | 0 | 0
Year 12 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.43 | 38.14 | 0 | 0
Year 13 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.44 | 41.93 | 0 | 0
Year 14 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.39 | 45.83 | 0 | 0
Year 15 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.37 | 48.58 | 0 | 0
Year 16 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.37 | 48.57 | 0 | 0
Year 17 | 2.78 | 2.33 | 0.81 | 0 | 0 | 3.36 | 48.56 | 0 | 0

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage | Grid usage
| % | % | % | % | %
Year 1 | 0.95 | 99.47 | 39.93 | 53.83 | 0
Year 2 | 2.26 | 98.59 | 32.47 | 52.77 | 0
Year 3 | 2.83 | 98.2 | 31.1 | 52.58 | 0
Year 4 | 5.98 | 95.85 | 25.03 | 49.78 | 0
Year 5 | 15.5 | 87.54 | 14.54 | 38.81 | 0
Year 6 | 16.46 | 86.5 | 12.98 | 37.43 | 0
Year 7 | 25.39 | 77.66 | 7.57 | 30.89 | 0
Year 8 | 25.51 | 77.52 | 7.44 | 30.78 | 0
Year 9 | 26.29 | 76.61 | 6.66 | 30.02 | 0
Year 10 | 26.66 | 76.25 | 6.59 | 29.85 | 0
Year 11 | 29.89 | 71.96 | 2.25 | 25.68 | 0
Year 12 | 29.99 | 71.87 | 2.27 | 25.64 | 0
Year 13 | 31.79 | 69.92 | 1.54 | 24.81 | 0
Year 14 | 33.56 | 68.01 | 1.02 | 23.6 | 0
Year 15 | 34.76 | 66.73 | 0.71 | 22.88 | 0
Year 16 | 34.76 | 66.74 | 0.74 | 22.88 | 0
Year 17 | 34.75 | 66.74 | 0.73 | 22.85 | 0

## Yearly energy parameters SC
| Generator share | Renewable penetration | Curtailment share | Battery usage | Grid usage
Component | Diesel Genset | PV panels | - | Battery bank | Grid
Scenario | 1 | 1 | 1 | 1 | 1
| % | % | % | % | %
Year 1 | 0.95 | 99.47 | 39.93 | 53.83 | 0
Year 2 | 2.26 | 98.59 | 32.47 | 52.77 | 0
Year 3 | 2.83 | 98.2 | 31.1 | 52.58 | 0
Year 4 | 5.98 | 95.85 | 25.03 | 49.78 | 0
Year 5 | 15.5 | 87.54 | 14.54 | 38.81 | 0
Year 6 | 16.46 | 86.5 | 12.98 | 37.43 | 0
Year 7 | 25.39 | 77.66 | 7.57 | 30.89 | 0
Year 8 | 25.51 | 77.52 | 7.44 | 30.78 | 0
Year 9 | 26.29 | 76.61 | 6.66 | 30.02 | 0
Year 10 | 26.66 | 76.25 | 6.59 | 29.85 | 0
Year 11 | 29.89 | 71.96 | 2.25 | 25.68 | 0
Year 12 | 29.99 | 71.87 | 2.27 | 25.64 | 0
Year 13 | 31.79 | 69.92 | 1.54 | 24.81 | 0
Year 14 | 33.56 | 68.01 | 1.02 | 23.6 | 0
Year 15 | 34.76 | 66.73 | 0.71 | 22.88 | 0
Year 16 | 34.76 | 66.74 | 0.74 | 22.88 | 0
Year 17 | 34.75 | 66.74 | 0.73 | 22.85 | 0